The same USE-2/RHW-2, 10 AWG cable is selected for all other system wiring, because it has the neces-

sary ampacity for each circuit.

A three -pole fused disconnect is selected to provide the PV and load disconnect functions and the neces-

sary overcurrent protection. The fuse selected is a RK-5 type, providing current limiting in the battery cir-

cuits. A pullout fuse holder with either Class RK-5 or Class T fuses could also be used for a more compact

installation. Fifteen amp fuses are selected to provide overcurrent protection for the 10 AWG cables. They are

used in the load circuit and will not blow on any starting surges drawn by the lamp or controller. The 15 -amp

fuse before the charge controller could be eliminated since that circuit is protected by the fuse on the battery

side of the charge controller. The disconnect switch at this location is required.

One of the two strings of PV modules could be subjected to reverse currents from the other string (1.25 x

4 = 5 amps) plus 15 amps from the battery through the 15 -amp fuse. If this 20 -amp potential backfed current

exceeds the module series fuse requirement, then the string fuses and a PV combiner must be added to the

system.

The equipment -grounding conductors should be 10 AWG conductors. An 8 AWG (minimum) conductor

would be needed to the ground rod.

The dc voltage ratings for all components used in this system should be at least 53 volts (2 x 21.3 x 1.25).

EXAMPLE 4 Remote Cabin DC -Only System

Array Size: 6, 12 -volt, 75 -watt modules; I

sc

= 4.8 amps, V.c = 22 volts

Batteries: 700 amp hours at 12 volts

Load: 75 watts peak at 12 -volts dc

Description

}NC1Y,S ROL

The modules are mounted on a rack on a hill

El

behind the house. Nonmetallic conduit is used to

1.4

0

8

2 AWG

EINIAL2

run the cables from the junction box to the control

(IN CONDUIT)

AWL, kl5E-2 ON

...EN, GROUND

panel. A control panel is mounted on the back

5AMP

porch, and the batteries are in an insulated box

2

AUG

CHARGE

under the porch. All the loads are dc with a peak-

CONTROLLER

OUT

20A

combined power of 75 watts at 12 volts due, pri-

NOTES

marily, to a pressure pump on the gravity -fed

052

1N,

AW444,04

RNA

FUSED

10.2W)

water supply. The battery bank consists of four

50N00

1114.50 <41456 AA/ 64440

015 CON NEC TO

44A4i

ONO NM

350 -amp -hour, 6 -volt, deep -cycle batteries wired

AWG

I

4444.

in series and parallel. Figure E-4 shows the system

350 Pk-tlf1V

RAM OILS

schematic.

Figure E-4. Remote Cabin DC -Only System

Calculations

The array short-circuit current is 28.8 amps (6 x 4.8).

CONTINUOUS CURRENT: 1.25 x 28.8 = 36 amps

80% OPERATION: 1.25 x 36.0 = 45 amps

The module interconnect wiring and the wiring to

a rack -mounted junction box will operate at 65°C. If USE-

2

cable with 90°C insulation

is chosen, then the temperature derating factor will be 0.58. The required

ampacity of the cable at 30°C is 62 amps (36/0.58),

which can be handled by 8 AWG cable with

an ampacity

of

80 amps in free air at 30°C. Conversely, the ampacity of the 8 AWG cable is 46.4 amps (80 x 0.58) at 65°C

which exceeds the 36 amp requirement.

A PV combiner with a fuse for each module will be required because the available potential short-circuit

current from these six modules in parallel plus the 45 -amps from the PV disconnect circuit breaker will far

exceed the maximum reverse current rating of a module.

From the rack -mounted

junction box to thecontrol panel, the conductors will be in conduit

n

Plrnrun afl

tr.

nnor

Tr ary

. .